{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["制剂土建","施德土建","原料土建"],"not_rendered":{"images":3,"defined_names":3,"comments":3},"read":"whole","date_system":"1900"}

{"sheet":"制剂土建","index":0,"n_rows":35,"n_cols":13,"rows_kept":35,"merged":[[0,0,0,11]]}
["工作量清单模板"]
["序号","单位","岗位","工程类别","名称","技术规格","材料","数量","单位","材料品牌","技术要求","备注"]
[1,"物流储运中心","中心库","土建工程","中心库卸车平台防撞条维修","1.拆除破损防撞条；                           2.调整防撞条、用膨胀螺丝固定安装防撞条。","橡胶",50,"条","无","施工后废料需清运出厂。","防撞条甲供、膨胀螺丝乙供。"]
[2,"物流储运中心","特药库","土建工程","麻药笼损坏维修","1.氩弧焊焊接维修破损麻药笼门5个；               2.更换4寸不锈钢折页更换16副；                3.更换不锈钢插销8个。","304不锈钢",1,"项","无","施工后不锈钢表面抛光清理干净。","材料乙供"]
[3,"物流储运中心","特药库","土建工程","特药库防盗门维修","1.拆除原有机械密码系统；                        2.更换调试新密码系统。","复合",1,"套","无","施工人员应具有“110”系统备案资质","材料乙供"," "]
[4,"物流储运中心","中心库","土建工程","电力电缆敷设","1.从一楼到配电室到总更三楼监控室ZRYJV-3*6敷设90米；        2.配电箱内空气开关安装，NXM-63S/3300 空气开关32A 利旧2台；  3.双电源自动转换开关安装12台，自动转换开关63A 开关利旧1台。","ZRYJV-3*6",90,"米","-","架空敷设，高度6米。","材料乙供"]
[5,"物流储运中心","中心库","土建工程","地廊堵漏维修","1.吊运地沟盖板，管道沟、管道井抽排水，管沟内人工挖淤泥、清理地沟4m³；                                                  2.管道沟内管线下方及周边带水堵漏、地廊内管线下方及周边带水堵漏，用高效速凝型堵漏灵堵漏；                               3.墙面轻钢龙骨，高强水泥板隔墙8㎡，墙面板缝嵌石膏、贴网格布，刮外墙防水腻子，刷外墙防水涂料10㎡；                   4.管沟上方予制混凝土盖板接头灌缝2m³，混凝土地面垫层 1m³。","-",1,"项","无","1.50mm国标龙骨,高强水泥板10mm厚； 2防水腻子份，防水涂料；          3.地沟防水保护层。                  4.施工脚手架自行考虑；            5.施工后垃圾需清运出厂 。            ","材料乙供"]
[6,"能源保障中心","张士供水","土建工程","张士消防水管路","消防水管路找漏点并机械挖掘履带式单斗液压挖掘机 斗容量0.8m3","——",150,"m3","无","寻找漏水点、抢修，履带式单斗液压挖掘机（斗容量0.8m3）预估5个台班。2.含大型机械设备进出场 履带式挖掘机进出场费","材料乙供"]
[7,"能源保障中心","张士供水","土建工程","张士消防水管路","消防水漏点并人工挖掘","——",15,"m3","无","带水挖泥，寻找漏水点。","材料乙供"]
[8,"能源保障中心","张士供水","土建工程","张士消防水管路","消防挖掘后潜水泵排水","——",16,"座·天","无","挖掘漏水点，潜水泵排水","材料乙供"]
[9,"能源保障中心","张士供水","土建工程","张士消防水管路","漏水点草地、树木挖掘恢复等","——",50,"m2","无","人工挖掘树木及恢复、人挖掘草地等进行平整（无法保活、需开春后重新种植）包赔","材料乙供"]
[10,"能源保障中心","张士供水","土建工程","张士消防水管路","回填砂保护管路","——",20,"m3","无","管线上方回填 中粗砂","材料乙供"]
[11,"能源保障中心","张士供水","土建工程","张士消防水管路","室外地面砖拆除、恢复","——",50,"m2","无","室外地面砖完整拆除","材料甲供"]
[12,"能源保障中心","张士供水","土建工程","张士消防水管路","垫层恢复","C20",50,"m2","无","地面混凝土垫层浇筑 C20，厚度为200mm","材料乙供"]
[13,"能源保障中心","张士供水","土建工程","张士消防水管路","老消防管路封堵","无缝钢管",4,"处","无","管路盲板在进行现浇灌注快干混凝土封闭","材料乙供"]
[14,"能源保障中心","张士供水","土建工程","张士地廊地廊蒸汽管线维修","保温及镀锌管壳拆除、恢复 DN150管线，60mm厚岩棉管壳，0.5mm厚镀锌板","——",2,"m","无","不停水、不停汽，在供汽用汽小的间隙内进行拆除作业，需要现场监测管线排水排汽量。","材料乙供"]
[15,"能源保障中心","张士供水","土建工程","张士地廊地廊蒸汽管线维修","阀门法兰处切割螺丝，松动螺丝，从法兰缝隙处泄水、排气。水泵抽排水，并观察水量大小，视水量切割管线、更换阀门水泵抽排水，观察水量。","——",2,"座·天","无","漏水点漏水需，潜水泵排水","材料乙供"]
[16,"能源保障中心","张士供水","土建工程","张士地廊地廊蒸汽管线维修","地廊蒸汽管线拆除 DN150","无缝钢管",2,"m","无","无缝钢管拆除","材料乙供"]
[17,"能源保障中心","张士供水","土建工程","张士地廊地廊蒸汽管线维修","J41H-16C-DN150 重型大体款 1.6Mpa T≤425℃;法兰金属垫","——",1,"台","无","安装DN150阀门（包括垫片、螺丝）。","材料乙供"]
[18,"能源保障中心","张士供水","土建工程","张士地廊地廊蒸汽管线维修","镀锌角钢，Φ12丝杆。","——",22,"kG","无","——","材料乙供"]
[19,"能源保障中心","张士供水","土建工程","张士地廊地廊蒸汽管线维修","钢质双排脚手架","——",16,"m2","无","脚手架高2m，宽2m、长8m","材料乙供"]
[20,"能源保障中心","张士供汽","土建工程","煤场立支撑柱","立一根φ133无缝钢管","——",7,"m","无","管除锈刷油（施工单位负责）并与煤棚焊接。","材料甲供"]
[21,"能源保障中心","张士供汽","土建工程","煤场立支撑柱","钢质双排脚手架","——",8,"m2","无","脚手架高6m、长4m、宽2m","材料乙供"]
[22,"能源保障中心","张士供汽","土建工程","煤场立支撑柱","做500mmX500mmX500mm一个基础墩","——",1,"个","无","C20混凝土浇筑，含基坑挖掘回填。","材料乙供"]
[23,"生活服务中心","张士办公楼","土建工程","铝扣板","600mm*600mm*1mm","铝",20,"m2","无","拆除、安装（龙骨修复）","材料乙供"]
[24,"生活服务中心","张士办公楼","土建工程","平板灯","600mm*600mm*36w/220v","复合",2,"盏","无","拆除、安装","材料乙供"]
[25,"生活服务中心","张士办公楼","土建工程","隔油池","吸污","——",2,"车/10立","——","水面无漂浮物","材料乙供"]
[26,"制剂检验中心","技术考察线及综合平台","土建工程","矿棉板顶棚拆除恢复","600*600","——",8,"m2","——","一层和三层顶棚及龙骨完好拆除、恢复，材料利旧，施工高度2.6m，需要配合架子施工","——"]
[27,"制剂检验中心","技术考察线","土建工程","室内墙面刮腻子、刷防霉涂料","——","——",10,"m2","——","原墙面砂纸打磨平滑，无需垃圾清运，施工高度2.6m","材料乙供"]
[28,"制剂检验中心","综合平台","土建工程","夹层内空调凝水管线阀门安装 DN40","双热熔活节铜阀门","铜阀门",2,"个","日丰、公牛","管线排水、泄水，施工高度3.6m","材料乙供"]
[29,"制剂检验中心","技术考察线","土建工程","夹层内凝水管线漏点安装哈夫节DN125","铸钢外壳（PE内衬）哈夫节 DN125*500 1个","铸钢",1,"个","——","管线排水、泄水，管线保温拆除，管线外表面机械除锈、打磨抛光。铸钢外壳（PE内衬）承压1.6MPa，施工高度3.2m","——"]
[30,"制剂检验中心","技术考察线","土建工程","夹层内热水管线焊制法兰盲板DN125","DN125","铸钢",1,"个","——","管线排水、泄水，管线保温拆除，管线外表面机械除锈，施工高度3.2m","材料乙供"]
[31,"制剂检验中心","生物检测线","土建工程","空调管线打孔焊制表冷器接头DN20三处共6个","管线上开孔，焊制表冷器接头","镀锌",6,"个","——","管线排水、泄水，管线保温拆除，管线外表面机械除锈，施工高度3.2m","材料乙供"]
[32,"制剂检验中心","技术考察线","土建工程","双排脚手架安装、拆除","钢质脚手架2*4m","——",5,"樘","——","安装拆除脚手架时对地面进行保护","材料乙供"]
[33,"制剂检验中心","综合平台","土建工程","肯德基门地弹簧更换维修","——","——",1,"樘","——","维修后开关方便，闭合严实","材料乙供"]

{"sheet":"施德土建","index":1,"n_rows":19,"n_cols":12,"rows_kept":19,"merged":[[0,0,0,10]]}
["工作量清单模板"]
["序号","单位","岗位","工程类别","名称","技术规格","材料","数量","单位","材料品牌","技术要求","备注"]
[1,"施德药业","口服固体制剂车间洁净区","土建工程","环氧自流平修复","洁净区各功能间多处开裂自流平地面清理，环氧砂浆5mm找平打磨后，按原颜色进行底涂和中涂，面漆修补，厚度2mm.共计154㎡。","环氧树脂",154,"m2","无","1.要求破损或裂痕处使用磨光机将破损处打磨掉，打磨面积不得小于裂痕面积的2倍，然后重新做局部重心的底涂、中涂、面图，要求颜色与原地面相同或相近。\n2.现场建筑垃圾清运；                   3、不需要基层处理；","材料乙供"]
[2,"施德药业","口服固体制剂车间洁净区","土建工程","洁净门维修","门锁修复，门体变形及破损处修复，底部加防风条，门框缝隙处做密封处理","铝合金门条及配套五金件",3,"樘","无","1.更换后固定无松动                         2.接口处密封连接                           3.水平开关，无刮地现象                    4.施工垃圾外运                          5.材料乙供","材料乙供"]
[3,"施德药业","口服固体制剂车间外包装","土建工程","顶板拆装","拆除、更换彩钢板棚顶8㎡。","单玻镁岩棉夹芯板",8,"m2","无","安装单玻镁岩棉夹芯板板8㎡，配套吊筋、槽铝、中字铝等。","材料乙供"]
[4,"施德药业","质量控制","土建工程","水钻钻孔","规格Φ50，数量1个，深度120mm","-",1,"项","无","施工垃圾清理外运。","材料乙供"]
[5,"施德药业","质量控制","土建工程","环氧自流平修复","效价准备室与效价室地面清理，环氧砂浆5mm找平打磨后，按原颜色进行底涂和中涂，面漆修补，厚度2mm.共计17㎡。","环氧树脂",17,"m2","无","1.要求破损或裂痕处使用磨光机将破损处打磨掉，打磨面积不得小于裂痕面积的2倍，然后重新做局部重心的底涂、中涂、面图，要求颜色与原地面相同或相近。\n2.现场建筑垃圾清运；                   3、不需要基层处理；","材料乙供"]
[6,"施德药业","质量控制","土建工程","新增自来水管路","新增自来水管路，直径DN20，壁厚2.5-3mm，加装不锈钢球阀和4分角阀各一个。","碳钢水管及五金件\n",20,"m","无","在技术夹层对接碳钢水管，要求焊接牢固，管路布置合理；","材料乙供"]
[7,"施德药业","质量控制","土建工程","增设烟感探头","新增房间增设烟感探头1个及弱点线（ZR-RVS2*1.0mm²）路铺设和消防系统点位需要授权并增加进控制系统增加。","探头及线路",15,"m","无","由消防维保公司提供技术支持，施工单位具体操作，甲方负责协调。","材料乙供"]
[8,"施德药业","质量控制","土建工程","增设紫外灯","新增一个三防紫外灭菌灯(单管、20w、管长600mm以内)","紫外灯具及灯管",1,"套","无","安装牢固；灯座打胶密封处理；灯管功率符合标准；独立开关控制；","材料乙供"]
[9,"施德药业","质量控制","土建工程","排水管路安装","DN50PVC排水管路安装及弯头和固定件。","PVC排水管",15,"m","无","1、排水管路安装包括直管段、排水弯头5个及卡箍膨胀螺丝等辅材；\n2、安装牢固无污水外溢；\n3、涉及高处作业打固定卡箍，安装高度3米；","材料乙供"]
[10,"施德药业","质量控制","土建工程","实验台切割就位","原房间试验台现场切割就位","-",1,"项","无","按照现场操作人员意见切割试验台并就位，试验台预估重量150kg，木质结构，切割长度为1.5m,板厚为20mm；","材料甲供"]
[11,"施德药业","质量控制","土建工程","房间安装铝蜂窝彩板门","安装2樘双开门（门高2100mm,宽1150mm，大扇900mm，小扇250mm,大扇上有玻璃窗高750mm，宽200mm)，彩板门包括门框、门锁等五金件，门底部需要有扫门条，双开门插销为暗装。","铝蜂窝彩板门，厚度为50mm",4.83,"m2","无","现场量尺制作，新门安装后不得有下沉刮地等现象，不得破坏其他彩钢板和地面等，门四周的包边处理美观；","材料乙供"]
[12,"施德药业","质量控制","土建工程","彩板安装","安装单玻镁50mm彩钢板，高2.6m，宽3.6m。","玻镁岩棉夹芯板",9.36,"m2","无","安装单玻镁岩棉夹芯板板9.36㎡，配套R角、槽铝，打胶处理等。","材料乙供"]
[13,"施德药业","质量控制","土建工程","彩钢板封窗","安装铝蜂窝彩板封窗，高1.6m 宽2.3m。","铝蜂窝彩板，厚度为50mm。",3.68,"m2","无","要求使用自攻钉锁死窗户活动扇；使用铝蜂窝彩板封窗，按照窗口尺寸密封，边封打胶处理；","材料乙供"]
[14,"施德药业","质量控制","土建工程","送风管路制作安装含风阀和散流板","长4000mm*宽300mm*高300mm*0.75mm","镀锌板",1,"个","无","现场制作镀锌板风管，连接原有支管后使用软连接对接铁质风阀（250*250），彩板开孔后安装铝制散流板（450*450）。","材料乙供"]
[15,"施德药业","质量控制","土建工程","试验台安装","楼内搬运试验台并安装就位连接上下水。","-",1,"项","无","效价准备室需立旧一个带水池的实验台（利旧），试验台预估150kg，楼内机械搬运，预计搬运距离为350m。","材料甲供"]
[16,"施德药业","质量控制","土建工程","安装86型明盒5孔插座","试验台安装10A斜五孔插座两个","斜五孔插座",2,"个","无","试验台安装10A斜五孔插座两个，新安，明装。","材料乙供"]
[17,"施德药业","质量控制","土建工程","墙壁插座电源线铺设","技术夹层中连接原有墙壁插座电源，铺设ZRBV2.5mm电源线15米，明装金属波纹管10米。","电源线、穿线管及其他电料",25,"m","无","1.电缆铺设不得有中间接头；\n2.电缆敷设后需做好线缆调试；\n3.自行考虑弯头等安装部分；\n4.管路支架稳固。","材料乙供"]

{"sheet":"原料土建","index":2,"n_rows":187,"n_cols":12,"rows_kept":187,"merged":[[0,0,0,10],[47,11,48,11],[72,11,76,11],[80,11,81,11]]}
["工作量清单模板"]
["序号","单位","岗位","工程类别","名称","技术规格","材料","数量","单位","材料品牌","技术要求","备注"]
[1,"201分厂","发酵","土建工程","玻璃钢修补","4油3布。","玻璃纤维布、玻璃钢树脂",30,"㎡","无","1.发酵四楼及楼顶环保玻璃钢管路漏点维修，维修面积共计30平方米，修补前打磨拉毛\n2.4油3布修补","材料乙供"]
[2,"201分厂","发酵","土建工程","下水疏通","φ110","无",2,"处","无","厂房卫生间下水疏通机疏通10米，疏通后排水正常。","材料乙供"]
[3,"201分厂","发酵","土建工程","地砖修复","600mm*600mm*10mm","地砖、水泥",5,"㎡","无","1.原有损坏的地砖拆除\n2.新地砖重新安装\n3.安装后表面平整，缝隙均匀美观","材料乙供"]
[4,"201分厂","发酵","土建工程","雨水井盖修复","——","水泥",3,"处","——","——","材料乙供"]
[5,"201分厂","提取","土建工程","洗漱间防水","打防水胶7㎡，更换瓷砖6㎡，规格300mm*300mm*4mm","防水胶",1,"项","——","1、拆安瓷砖瓷砖颜色与现场一致                      2、残土外运","材料乙供"]
[6,"201分厂","提取","土建工程","雨水井盖修复","——","水泥",7,"处","——","——","材料乙供"]
[7,"201分厂","转化","土建工程","后部女卫生间墙面瓷砖更换","配合水泥砂浆更换瓷砖面积8㎡，规格300mm*600mm*8mm","瓷砖","8","㎡","无","1、破损瓷砖清理，基层处理\n2、施工垃圾外运","材料乙供"]
[8,"201分厂","转化","土建工程","前部2楼卫生间更换下水管","PPR/DN50mm*厚度5m",1,"米","个","无","1、更换后通畅","材料乙供"]
[9,"201分厂","转化","土建工程","污水井密封","——","发泡胶",9,"个","无","/1、用发泡胶从井内填充井筒与井圈的缝隙，封严，不透气\n2.井圈与地面间缝隙用碎石填充，地面平整，不露出玻璃钢井筒","材料乙供"]
[10,"201分厂","转化","土建工程","污水井清掏","8m³","吸污车",4,"处","——","1、吸水车进行污水井内杂物及淤泥清掏，井内掏干净，不要造成现场地面污染","材料乙供"]
[11,"201分厂","转化","土建工程","排风扇更换","200mm*200mm","排风扇",3,"个","——","卫生间更换排风扇安装后运行正常","尺寸以实际测量为准，材料乙供"]
[12,"201分厂","转化","土建工程","下水疏通","φ110mmPPR","——",3,"处","无","1.确保下水畅通","材料乙供"]
[13,"201分厂","转化","土建工程","精母下水管维修","φ110mmRRP","——",3,"处","无","1、下水管三通处热熔焊接管道处理干净，热熔焊接","材料乙供"]
[14,"201分厂","精制工段","土建工程","小便器更换感应器","小便池更换感应器水阀一套，更换软连接2根，","小便感应器、软连接",1,"套","——","密封严密，感应开关灵敏","材料乙供"]
[15,"201分厂","精制工段","土建工程","地弹簧","门厅玻璃门更换地弹簧一个","地弹簧",1,"个","——","开关灵活，速度适中","材料乙供"]
[16,"201分厂","精制工段","土建工程","厕所更换脚踏阀","更换脚踏阀DN25，数量2个","不锈钢",2,"个","——","无泄漏","材料乙供"]
[17,"201分厂","精制工段","土建工程","厕所脚踏阀冲水管更换","更换脚踏阀冲水管DN25，0.5m两处","PPR","1","m","——","无泄漏","材料乙供"]
[18,"201分厂","精制工段","土建工程","厕所瓷砖更换","更换瓷砖300mm*300mm*5mm","瓷砖",2,"块","——","外观平整","材料乙供"]
[19,"201分厂","精制","土建工程","疏通下水","1.疏通PL-4二楼至三楼DN100下水道30m。","疏通器",30,"m","无","疏通后水流通常，现场整洁","材料乙供"]
[20,"201分厂","张士功辅楼","土建工程","地砖拆除","拆除300mm*300mm地砖，铺设600mm*600mm 防滑","——",20,"m2","——","1.地面基层清理\n2.地面找平\n3.铺设地砖\n4.施工垃圾清运\n5.拆除地砖将下水口封堵，避免施工垃圾进入下水管道","材料乙供"]
[21,"201分厂","张士功辅楼","土建工程","排水管","外径110mm*5mm","UPVC管",15,"米","——","拆除原排水管，更换D110排水管5米，直通3个，拆除水管按要求放置到指定位置。","材料乙供"]
[22,"201分厂","张士VC-Na","土建工程","地砖更换","600mm*600mm*25mm","花岗岩地砖",10,"㎡","——","1.拆除原破损花岗岩至基层。\n2.更换铺贴600mm*600mm*25mm花岗岩。\n3.水泥灌缝。\n4.施工垃圾清运。","材料乙供"]
[23,"201分厂","颗粒","土建工程","更换下水管","外径110mm*厚3.5mm","铸铁",20,"米","——","1.拆除原PVC管\n2.更换D110铸铁下水管\n3.安装配套法兰8片,弯头2个，三通1个","材料乙供"]
[24,"201分厂","颗粒","土建工程","铸铁管密封更换","外径110mm","橡胶",8,"个","——","拆开铸铁管法兰及密封，更换密封","材料乙供"]
[25,"201分厂","张士VC-Na","土建工程","防爆窗口维修","——","水泥砂浆",0.1,"m2","——","对破损窗口清根处理，水泥砂浆填补维修，高度6米。","材料乙供"]
[26,"201分厂","压缩饼干生产线","土建工程","晾衣架安装","2700mm长 双杆","S30408晾衣架",1,"个","--","1、晾衣架安装紧固\n2、施工垃圾外运","材料乙供"]
[27,"201分厂","压缩饼干生产线","土建工程","水钻眼","外径110mm*5mm","——",1,"个","——","透眼","材料乙供"]
[28,"201分厂","压缩饼干生产线","土建工程","地漏安装","外径110mm*5mm","30408地漏",1,"个","——","——","材料乙供"]
[29,"201分厂","压缩饼干生产线","土建工程","下水管安装","外径110mm*5mm","UPVC管",3,"米","——","连接地漏至排水干线，弯头1个、三通1个","材料乙供"]
[30,"201分厂","张士VC-Na","土建工程","彩板拆除","1200mm*3500mm","岩棉夹芯板",3,"张","——","拆除配套R角，槽铝","材料乙供"]
[31,"201分厂","张士VC-Na","土建工程","洁净窗拆安","1200mm*1200mm","双层玻璃",1,"扇","——","拆除配套框架，更换新框架","材料乙供"]
[32,"201分厂","系列工段","土建工程","安装彩板","单玻镁 50mm","玻镁岩棉夹芯板",65,"㎡","——","安装单玻镁岩棉夹芯板板65㎡，配套R角、槽铝、中字铝、打胶等。","材料乙供"]
[33,"201分厂","细河厂区","土建工程","安装彩板门","1500mm*2100mm*50mm","岩棉夹芯板",1,"樘","——","安装岩棉夹芯板彩板门1樘，配套门料、门锁、门鼻儿。","材料乙供"]
[34,"201分厂","压缩饼干生产线","土建工程","风机吊架加固","管道式通风机 1000mm*1000mm*800mm ","角钢",1,"台","——","1.利用现有吊点将风机复位。\n2.支架上方增加减震胶垫。\n3.恢复两侧吊架，采用电弧焊焊接的方式加固。\n4.增加2处吊点，并制作吊架，使风机达到6点固定。","材料乙供"]
[35,"201分厂","办公楼","土建工程","下水维修","600mm*600mm*10mm瓷砖8块，蹲便池内径25mm","瓷砖",1,"项","无","1、瓷砖拆除并恢复\n2、恢复的瓷砖颜色与现场尽量保持一致\n3、1、更换蹲便池1套\n4、拆除更换损坏脚踏阀2个\n5.安装严密无泄漏\n6、施工垃圾外运","材料乙供"]
[36,"201分厂","办公楼","土建工程","水池子下水管维修","直径25mm","——",4,"处","无","维修更换后无渗漏","材料乙供（实际尺寸具体测量为准）"]
[37,"201分厂","单磷酸酯","土建工程","沉降池","长4000mm*宽2000mm*高1500mm","挖掘机、电镐",12,"m³",null,"1、施工挖掘长4000mm*宽2000mm*高1500mm的长方形池，底部人工找平，铺垫 10cm 厚碎石垫层并夯实。\n2、施工垃圾外运","材料乙供"]
[38,"201分厂","单磷酸酯","土建工程","沉降池","长4000mm*宽2000mm*高1500mm","C30混凝土",6,"m³",null,"1、方形池分三个区域，1#为积泥池，2#为沉降池，3#为管道泵检修池，各分区中间需支钢模（钢筋直径12mm），浇筑 C30 混凝土（厚度 15cm），振捣密实，养护 7 天。\n2、1#和2#分区中间钢模板高度1m，2#与3#分区中间模板高度1.5m。\n3、施工垃圾外运。","材料乙供"]
[39,"201分厂","单磷酸酯","土建工程","沉降池","长4000mm*宽2000mm*高1500mm","聚氨酯防水涂料及水泥砂浆",50,"㎡",null,"1、内壁干燥后刷防水涂料2遍，安装地埋出口管道并做好密封。防水做完后需进行闭水试验24小时。\n2、对防水层进行保护，做水泥砂浆保护层，厚度 20mm，采用 1:3 水泥砂浆抹面，压实抹光，养护至强度达标。\n3、施工垃圾外运","材料乙供"]
[40,"201分厂","单磷酸酯","土建工程","泵检修区","厚度20mm","页岩砖、水泥砂浆",5,"㎡",null,"1、砖砌步行梯检修；用 MU10 页岩砖（或混凝土实心砖）砌筑台阶主体，外侧及踏面、踢面用 1:2.5 防水水泥砂浆抹面（厚度 20mm），必要时掺防水剂提升抗渗性。\n2、施工垃圾外运","材料乙供"]
[41,"201分厂","单磷酸酯","土建工程","沉降池支撑格栅板","G325/30/100","热镀锌格栅板",8,"㎡",null,"1、沉降池外边缘修建格栅板放置边缘台，格栅板搭接边缘台支撑宽度50mm，格栅板选用G325/30/100（32mm×5mm 扁钢，30mm 扁钢间距，100mm 横杆间距）","材料乙供"]
[42,"201分厂","单磷酸酯","土建工程","沉降池护栏","高度1.2m*长度12m","铁马护栏（碳钢）",12,"m",null,"1、市政铁马护栏；框架式结构，喷塑防锈，高度 1.2m 左右，单节长 1.5~2m，可拼接。","材料乙供"]
[43,"201分厂","单磷酸酯","土建工程","排水管","外径110mm*5mm","PPR",14,"米",null,"1、安装FRPP带篦子地漏2个。2、安装聚丙烯管110*10排水管路安装14米，弯头5个，直通2个，三通1个。3、施工垃圾外运","材料乙供"]
[44,"201分厂","单磷酸酯","土建工程","暗沟","宽200mm*深50mm","水泥砂浆、环氧自流平",20,"㎡",null,"1、使用机械开挖那宽度200mm深度50mm的暗沟将排水管引至沉降池内。2、完成后水泥砂浆找平，上面罩环氧自流平。3、施工垃圾外运。","材料乙供"]
[45,"201分厂","单磷酸酯","土建工程","铺设电缆槽","宽150mm*深100mm","热镀锌线缆槽、穿线管、吊架",20,"米",null,"1、施工队伍铺设线缆槽20米。2、安装防爆操作柱1个。3、安装穿线管20米。4、制作安装吊架10处。5、墙体开孔一处，线缆槽铺设完毕后线缆槽与墙体缝隙水泥砂浆填充抹平，墙面粉刷聚氨酯涂料。6、施工垃圾外运。","材料乙供"]
[46,"201分厂","发酵","土建工程","脚手架","2000mm*1200mm*4000mm，发酵5座，提取5座，转化7座，综合保障3座，精致2座，系列2座，单磷酸酯2座","碳钢",26,"座","无","1、脚手架\n2、符合安全要求","材料乙供，月度例行工作：用于高空设备、管路系统的自主维修保养，以及高空区域卫生清洁作业，保障设备设施持续稳定运行；\n应急检修场景：当发生设备故障（如气源管漏气等）时，作为临时安全作业平台，支撑快速响应检修，及时排除安全隐患、恢复系统正常运行。"]
[47,"201分厂","提取","土建工程","管架","4000mm*2000mm*4000mm","碳钢",5,"座","无","1、脚手架\n2、符合安全要求"]
[48,"202分厂","后部工段","土建工程","更换防火门","2350mm*2100mm","防火门",2,"樘","——","1.符合防火要求。\n2.安装完成后清理现场\n3.旧门拆除后移至预留区指定地点，距离50米","材料乙供"]
[49,"202分厂","后部工段","土建工程","下水管疏通，后部5处，前部5处","φ110","FRPP",10,"处","——","用疏通器疏通下水","材料乙供"]
[50,"202分厂","后部工段","土建工程","小便池维修","130mm*130mm","——",3,"处","——","1.小便池感应器失灵更换5个，重新打胶固定。\n2.小便池下水管泄漏维修3处。","材料乙供"]
[51,"202分厂","后部工段","土建工程","降膜玻璃钢短节更换","DN300,厚5mm，长度300×750","酚醛玻璃钢",1,"个","——","制作DN300*750法兰酚醛玻璃钢短节1个。耐盐酸、醋酸","材料乙供"]
[52,"202分厂","后部工段","土建工程","降膜玻璃钢短节更换","DN300*长750*厚5mm","防酸碱玻璃钢",1,"个","——","拆除并安装冷凝器与储罐连接DN300*750法兰酚醛玻璃钢短节1个","材料乙供"]
[53,"202分厂","后部工段","土建工程","搭设脚手架","4m*2m*2m\n1.二楼中和搭设1幅\n2.环合岗位拆除废旧电缆搭设4幅。\n3.岗位刷油搭设8幅\n4.洁净区内清洁搭设5幅","—",15,"座","无","1.符合安全要求，配备格证。\n2.用完后及时拆除，清理现场。\n3.结晶区内搭设注意保护地面","材料乙供"]
[54,"202分厂","后部工段","土建工程","搭设脚手架","6m*2m*2m\n1.洁净区内清理高效出口搭设 5幅\n2.洁净区内彩板打胶搭设5幅。\n","—",8,"座","无","1.符合安全要求，配备格证。\n2.用完后及时拆除，清理现场。\n3.结晶区内搭设注意保护地面","材料乙供"]
[55,"202分厂","前部工段","土建工程","成环回汽管更换搭设脚手架","2m*4m*5m","木质",5,"个","——","按现场需要进行分批次搭设","材料乙供"]
[56,"202分厂","前部工段","土建工程","二楼甲醇塔搭设脚手架","4m*1.5m*4m","碳钢",6,"个","——","按现场需要进行分批次搭设","材料乙供"]
[57,"202分厂","前部工段","土建工程","室外废水管路维修搭设脚手架","6m*1.5m*6m","碳钢",5,"个","——","按现场需要进行分批次搭设","材料乙供"]
[58,"202分厂","前部工段","土建工程","下水管维修","φ110","FRPP",5,"处","——","下水管路弯头维修5处","材料乙供"]
[59,"202分厂","前部工段","土建工程","更换防火门","2300mm*2100mm","防火门",2,"樘","——","1.符合防火要求，安装完成进行墙面漆恢复，要求与原有漆色一致\n2.安装完成后清理现场\n3.旧门拆除后移至预留区指定地点，距离50米\n4.安装闭门器2台。","材料乙供"]
[60,"202分厂","前部工段","土建工程","玻璃门维修","1800mm*2100mm","——",1,"樘","——","1.更换门轴及地弹簧\n2.维修后保证门开关顺畅","材料乙供"]
[61,"203分厂","吡拉西坦","土建工程","甲苯尾气回收装置喷淋塔堵漏及更换垫片","碱洗塔人孔接头修补漏点1处，裂痕为200mm,碱洗塔人孔接头尺寸为DN300:重新涂环氧玻璃钢树脂，四布五油","玻璃钢防腐材料",1,"处","无","1、试漏要求无漏点\n2、保证平整和紧密贴合要求涂层平整、光滑\n3、施工后现场完成清理","材料乙供"]
[62,"203分厂","吡拉西坦","土建工程","成盐泵房真空泵基础拆除及恢复","真空泵基础(1620mm*920mm*105mm)拆除至露出槽钢拍子，基础花岗岩理石拆除。甲方重新加固真空泵底座后，乙方恢复基础，并使用水泥重新贴花岗岩理石饰面，单块花岗岩理石尺寸为600mm*600mm*25mm,材料乙供","水泥、花岗岩砖",2,"㎡","无","1、拆开花岗岩砖，清理背面水泥\n2、采用直接抹水泥砂浆粘贴法，调制1:2水泥沙浆\n3、使用水平尺保证垂直度\n4、要求拼接严密，接缝顺直\n5、施工废料需清运出厂","材料乙供"]
[63,"203分厂","吡拉西坦","土建工程","洁净区技术夹层调节风量","检查并调节洁净区技术夹层镀锌管进回风管阀门，调节一楼各功能间风量，确保各房间压差符合标准。","静压箱",4,"处","无","1、调节风量后洁净区压差满足要求","材料甲供"]
[64,"203分厂","硫糖铝","土建工程","洁净区棚上开孔","洁净区碰上钻φ25mm彩钢板孔洞","彩钢板",3,"个","无","1、要求钻头安装集尘罩\n2、登高作业，作业高度为5m\n3、清理孔洞周围灰尘","材料乙供"]
[65,"203分厂","硫糖铝","土建工程","洁净区棚上开孔","洁净区碰上钻φ20mm彩钢板孔洞","彩钢板",3,"个","无","1、要求钻头安装集尘罩\n2、登高作业，作业高度为5m\n3、清理孔洞周围灰尘","材料乙供"]
[66,"203分厂","硫糖铝","土建工程","开孔不锈钢装饰环","洁净区安装φ25mm不锈钢装饰环","装饰环",3,"个","无","1、材料乙供\n2、装饰环安装牢固\n3、登高作业，作业高度为5m\n4、清理装饰环表面浮灰","材料乙供"]
[67,"203分厂","硫糖铝","土建工程","开孔不锈钢装饰环","洁净区安装φ20mm不锈钢装饰环","装饰环",3,"个","无","1、材料乙供\n2、装饰环安装牢固\n3、登高作业，作业高度为5m\n4、清理装饰环表面浮灰","材料乙供"]
[68,"204分厂","左卡精制","土建工程","压差调节","调试各高效送风风阀，400*400*95 21个；550*550*95 28个；630*630*95 6个。","——",55,"个","——","压差调节后，按照精烘包管理规定要求，符合现场环境使用要求。技术夹层内施工，作业高度4-8米。\n","——"]
[69,"204分厂","左卡精制","土建工程","瓷砖修复","300mm*600mm*20mm色瓷砖","瓷砖",0.5,"㎡","——","1.1处瓷砖修补，原有瓷砖清除，更换瓷砖\n2.施工垃圾清运\n3.材料乙供","——"]
[70,"204分厂","肉碱王岗位","土建工程","肉碱王外包卸爆窗贴隔热膜","卸爆窗贴隔热膜","隔热膜",20,"㎡","——","1.材料乙供，现场安装。\n2.作业高度2米。\n3、做好窗户框封堵封边。  \n4.乙方负责所有垃圾的清运。","  "]
[71,"204分厂","系列工段","土建工程","更换下水管变径","φ110变φ63","FRPP",3,"个"," ——","1.拆安、更换变径\n2.材料乙供","乙酰操作台上母液管及回流管"]
[72,"204分厂","系列工段","土建工程","更换下水管法兰","DN100","FRPP",3,"片"," ——","1.拆安、更换法兰\n2.材料乙供"]
[73,"204分厂","系列工段","土建工程","更换下水管法兰","DN50","FRPP",3,"片"," ——","1.拆安、更换法兰\n2.材料乙供"]
[74,"204分厂","系列工段","土建工程","更换下水管","φ110*5mm","FRPP",1.2,"米"," ——","1.拆安、更换下水管\n2.材料乙供"]
[75,"204分厂","系列工段","土建工程","更换下水管","φ63*3mm","FRPP",1.2,"米",null,"1.拆安、更换下水管\n2.材料乙供"]
[76,"204分厂","回收塔","土建工程","管路冷保温制作","φ76mm管路安装冷保橡塑50mm厚，\n外包0.5mm铝板。","橡塑棉/铝板",2,"m2","——","1.作业高度3-7米\n2.施工垃圾外运\n3.材料乙供","乙二醇管路保温制作"]
[77,"204分厂","回收塔","土建工程","阀门冷保温制作","DN65流量计安装冷保橡塑50mm厚，\n外包0.5mm铝板。","橡塑棉/铝板",2,"个","——","1.作业高度3-7米\n2.施工垃圾外运\n3.材料乙供","乙二醇管路保温制作"]
[78,"204分厂","回收塔","土建工程","钢质门防盗门","高1980mm*宽1470mm","防火门",1,"樘"," ——","1.126C厂房回收塔风机房岗位钢质门更换1樘，旧门拆除清运，新门安装。\n2.内门框与墙体缝隙水泥砂浆填充抹平，大白恢复，外门框与墙体缝隙水泥砂浆填充抹平，外墙涂料恢复。 \n3.施工垃圾清理，外运。\n4.材料乙供。","回收塔风机房"]
[79,"204分厂","PG05一楼","土建工程","更换安装铸铁下水管","φ108*4mm","铸铁管",11,"米"," ——","1.作业高度1-6米。 \n2.材料乙供\n3.施工垃圾外运\n4.乙方负责搭架子，长6米*宽2米 \n5.安装完成后试漏，确保其密封性","PG05一楼下水维修"]
[80,"204分厂","PG05一楼","土建工程","更换安装铸铁管件","φ108*4mm三通2个，下水弯2个，法兰14个，管箍3个，","铸铁三通",1,"项"," ——","1.作业高度6米。 \n2.材料乙供\n3.施工垃圾外运\n4.乙方负责搭架子，长6米*宽2米 \n5.安装完成后试漏，确保其密封性"]
[81,"204分厂","PG05一楼","土建工程","管路冷保温制作","φ76mm管路安装冷保橡塑50mm厚，\n外包0.5mm铝板。","橡塑棉/铝板",3,"米","——","1.作业高度3-7米\n2.施工垃圾外运\n3.材料乙供","乙二醇管路保温制作"]
[82,"204分厂","系列工段","土建工程","压差调节","调试各高效送回风风阀，400*400*95 22个；550*550*95 23个；630*630*95 6个，符合现场环境使用要求（高效总计51个）。","——",51,"个","——","1.压差调节后，按照精烘包管理规定要求，符合现场环境使用要求              \n2.需受限空间作业                  \n3.压差调节后保证半年好用  ","酒盐精烘包"]
[83,"204分厂","左卡前部右旋","土建工程","工艺排气管道更换","DN200*6.5mm玻璃钢风管21米，DN200*6.5mm玻璃钢弯头1个","玻璃钢",1,"项","——","1.依据现场要求安装\n2.材料乙供\n3.作业高6米\n4.玻璃钢管道开孔5处，工艺排气管道重新连接\n5.原有玻璃钢管道拆除清运\n6.连接处玻璃钢树脂3布4油","老化工艺排气管更换"]
[84,"204分厂","左卡前部右旋","土建工程","工艺排气管道更换","DN200玻璃钢管漏点封堵","玻璃钢",2,"处","——","1.玻璃钢管道封堵漏点2处玻璃钢树脂3布4油\n2.材料乙供\n3.作业高6米"]
[85,"204分厂","左卡前部右旋","土建工程","工艺排气管道更换","DN150*5mm玻璃钢风管","玻璃钢",9,"米","——","1.依据现场要求安装\n2.材料乙供\n3.作业高4米\n4.原有玻璃钢管道拆除清运\n5.连接处玻璃钢树脂3布4油"]
[86,"204分厂","胺化","土建工程","窗膜","厂房窗户遮光窗膜","遮光窗膜",24,"㎡","无","1.窗户原有贴膜清理，窗膜重新粘贴。\n2.材料乙供，作业高度4-6米。","——"]
[87,"204分厂","左卡前部","土建工程","搭设钢管架","长2m*宽3m*高5m"," ——",15,"座"," ——","按现场需要进行分次搭设，并符合安全要求。","配合分厂日常检修"]
[88,"204分厂","204分厂水解","土建工程","防火门维修","1.防火门维修1樘，防火门1750mm*高2080mm","复合",1,"樘","——","1.更换门折页4个，门板水平安装\n2.门框上方水泥横梁修正\n3.墙体缝隙水泥砂浆填充抹平，大白恢复\n4.材料乙供","空调机房"]
[89,"204分厂","PG05","土建工程","大白修复","1.半缩醛操作间顶棚大白修补粉刷涂料\n2.旋转蒸发器室顶棚大白修补粉刷涂料\n3.15甲反应室顶棚大白粉刷涂料\n4.成品反应室顶棚大白粉刷涂料\n","内墙乳胶漆涂料/石膏",52,"m²","——","1.大白涂料粉刷\n2.将原有破损大白进行清根处理\n3.材料乙供\n4.作业高度7米\n5.施工垃圾乙方负责清理外运\n6.乙方负责搭架子","三楼顶棚大白修复"]
[90,"204分厂(研发费)","多功能","土建工程","126C厂房北侧卸爆窗贴隔热膜","卸爆窗贴隔热膜","隔热膜",156,"㎡","——","1.材料乙供，现场安装。\n2.作业高度7米，室内两侧搭架子。              3.对玻璃进行清洁后粘贴，要求无浮尘无气泡。\n4.做好窗户框封堵封边。  \n5.乙方负责所有垃圾的清运至甲方指定地点。","126C厂房北侧"]
[91,"204分厂(研发费)","多功能","土建工程","下水管","φ110*6mm","UPVC",10,"米","——","1.施工垃圾外运，材料乙供\n2.下水管路维修后，管路恢复与主管路链接","2楼蒸汽室"]
[92,"204分厂(研发费)","多功能","土建工程","下水管管箍","φ110*6mm管箍4个，弯头4个","UPVC",1,"项","——","1.施工垃圾外运，材料乙供\n2.下水管路维修后，管路恢复与主管路链接","2楼蒸汽室"]
[93,"204分厂(研发费)","多功能","土建工程","管路冷保温制作","φ108mm管路安装冷保橡塑50mm厚，\n外包0.5mm铝板。","橡塑棉/铝板",3,"m2","——","1.作业高度3-7米\n2.施工垃圾外运\n3.材料乙供","乙二醇管路保温制作"]
[94,"204分厂(研发费)","多功能","土建工程","阀门冷保温制作","DN100流量计安装冷保橡塑50mm厚，\n外包0.5mm铝板。","橡塑棉/铝板",2,"个","——","1.作业高度3米\n2.施工垃圾外运\n3.材料乙供","乙二醇管路保温制作"]
[95,"204分厂(研发费)","多功能","土建工程","天圆地方镀锌风管","0.5mm厚镀锌板","镀锌板",1,"个",null,"1.制作方700mm*700mm,圆周长2000mm,高950mm镀锌风管，∠50mm*3mm镀锌角铁3000mm。  \n2.原风管拆除，新风管安装。              3.施工垃圾外运，放到指定地点。          4.材料乙供。\n5.不涉及登高作业。","楼顶风管"]
[96,"204分厂(研发费)","多功能","土建工程","风管软连接制作","风管软连接制作长1700mm*宽300mm（防水材质）","——",1,"个","——","1.原有破损软连接拆除，新软连接安装。    2.材料乙供。        \n3.施工垃圾外运。\n4.不涉及登高作业。","楼顶风机软连接"]
[97,"204分厂(研发费)","多功能","土建工程","PVC墙板","厚5mm,PVC墙板","PVC",130,"平方米","——","1.安装PVC墙板所有缝隙打胶，地面、棚顶墙角交接位置安装阴角阳角。                 \n2.U型50 50*15*1.2mm轻钢龙骨。             3.窗口包上，需加护角。               4.材料乙供。        \n5.施工垃圾外运。","外环廊"]
[98,"204分厂(研发费)","多功能","土建工程","钢质门防盗门","高2200mm*宽1600mm","钢质防盗门",1,"樘"," ——","1.126C厂房小产品岗位钢质门更换1樘，旧门拆除清运，新门安装。\n2.内门框与墙体缝隙水泥砂浆填充抹平，大白恢复，外门框与墙体缝隙水泥砂浆填充抹平，外墙涂料恢复。 \n3.施工垃圾清理，外运。\n4.材料乙供。","小产品"]
[99,"205分厂","一工段","土建工程","钢管插架","1.5m*2m*4m","钢管卡扣",10,"座","——","1.高处管路漏点维修，设备维修，灯具更换，气源接头更换；\n2.1.5m*2m*4m。","主辅材乙供"]
[100,"205分厂","一工段","土建工程","钢管卡扣架子搭设","4m*4m*8m","钢管卡扣",10,"座","——","1.钢管卡扣架子，维修高处设备，高处管路漏点或安装管路支架钢管插架无法搭设时使用；\n2.2m*4m*6m。","主辅材乙供"]
[101,"205分厂","一工段","土建工程","木制架子搭设","1m*1m*4m","防腐木质",10,"座","——","1.木制架子，狭小空间维修作业使用；\n2.1m*1m*4m。","主辅材乙供"]
[102,"205分厂","一工段氢化","土建工程","下水管疏通","φ108","——",2,"处","——","1.疏通氢化厂房一楼生活区下水管路2处，疏通完毕后下水管路畅通。","主辅材乙供"]
[103,"205分厂","一工段酯化","土建工程","围堰砌筑","120mm*150mm红砖25米，水泥砂浆厚度20mm","红砖",1,"项","——","1.清理原有破损围堰后进行重新砌筑围堰；\n2.红砖连接处使用水泥砂浆进行粘接；\n3.对红砖砌筑的围堰进行抹灰找平\n4.施工垃圾由施工方进行清理。","主辅材乙供"]
[104,"205分厂","一工段酯化","土建工程","地面恢复","600mm*600mm，\n厚度：20mm","花岗岩",20,"㎡","——","1.酯化厂房地面破损地砖清理干净；\n2.使用水泥砂浆将塌陷不平地面找平、填实，然后铺设地砖；\n3.施工垃圾进行分类，不可回收垃圾需要施工方负责处理，施工垃圾日清。","主辅材乙供"]
[105,"205分厂","一工段酯化","土建工程","防盗门","1.5m*2.3m","——",4,"樘","——","1.拆除原有防盗门，重新安装固定防盗门；\n2.防盗门需打膨胀螺栓固定，密封处使用发泡密封；\n3.防盗门佩戴相应门锁及闭门器；\n4.废弃门清运至指定地点（500m以内）。","主辅材乙供"]
[106,"205分厂","一工段精制","土建工程","彩板维修","50mm厚","双玻镁彩板",30,"㎡","——","1.拆除损坏双玻镁彩板30㎡\n2.安装新的双玻镁彩板30㎡（彩板利旧20㎡，更换10㎡），新安装的彩板需要使用通丝等固定三件套对彩板进行固定；\n3.彩板连接处使用R角、外圆柱转角等进行连接并使用密封胶进行密封；\n4.恢复照明4盏\n5.拆卸的废旧彩板运至甲方指定地点存放","主辅材乙供"]
[107,"205分厂","二工段","土建工程","手盆反水弯下水管","——","不锈钢",9,"个","——","1.拆除洗手盆下水管9套\n2.安装洗手盆反水弯下水管9套。\n","材料乙供"]
[108,"205分厂","二工段","土建工程","男士小便池感应器","——","感应器、地排",3,"套","——","1.拆除原有小便池出水管件。\n2.安装新的男士小便池反水弯下水管3套\n3.安装小便池感应器3套.（涉及管路改造）\n","材料乙供"]
[109,"205分厂","二工段","土建工程","卫生间轴流风机","SFG型、风量600m³/h转数1450r/min、电机功率0.06KW","碳钢",1,"台","——","1.拆除原有卫生间轴流风机1台。\n2.安装新的轴流风机及软连接恢复。\n3.施工垃圾乙方负责处理。","材料乙供"]
[110,"205分厂","办公室","土建工程","门厅地弹门维修","——","地弹簧",1,"套","——","1.拆除原有损坏地弹簧1套\n2.重新安装新的地弹簧1套\n3.调节门开关速度，维修后地弹门可自行关闭，门缝对齐。","材料乙供"]
[111,"205分厂","氨盐","土建工程","门厅雨大玻璃更换","1500mm*2000mm","双层钢化玻璃",1,"块","——","1.拆除损坏的雨搭双层钢化玻璃1块\n2.安装新的双层钢化玻璃1块\n3.作业高度3米","材料乙供"]
[112,"206分厂","反应岗位","土建工程","搭架子","2m*2m*5m","——",5,"个","——","搭设钢管卡扣架，符合安全要求，悬挂合格证。","维修物料管路使用"]
[113,"206分厂","反应岗位","土建工程","搭架子","2m*2m*7m","——",2,"个","——","搭设钢管卡扣架，符合安全要求，悬挂合格证。","维修电动葫芦使用"]
[114,"206分厂","反应岗位","土建工程","围堰","宽140mm高150mm","红砖/水泥",10,"米","——","1.残土外运。\n2.颜色与现场一致。","材料乙供"]
[115,"206分厂","调度室","土建工程","地沟盖板","长5500mm*宽285mm*厚2mm哑光不锈钢板",304,1,"处","——","1.拆除旧盖板，倒运至指定地点存放。\n2.安装哑光不锈钢盖板，切割四段安装，打胶与地面固定。","材料乙供"]
[116,"206分厂","分馏岗位","土建工程","搭架子","2m*2m*4m","——",4,"个","——","搭设钢管卡扣架，符合安全要求，悬挂合格证。","维修物料管路使用"]
[117,"环保处理中心","除臭间西侧","土建工程","钩机开挖","50m*1.5m深","——",1.5,"台班","——","斗容量0.8m³履带钩机挖土及回填，进出场需拖板车拖运一台次，人工配合1.5工日","材料乙供"]
[118,"环保处理中心","除臭间西侧","土建工程","玻璃钢管道","安装DN300玻璃钢（承重力8KN）","——",50,"m","——","管路安装需放坡、管路之前使用胶圈连接","材料乙供"]
[119,"环保处理中心","除臭间西侧","土建工程","更换玻璃钢井","拆除原有渗漏的DN800*15000mm砖砌井，更换安装DN1000*15000mm的玻璃钢","——",2,"个","——","拆除原有渗漏井、更换安装的玻璃钢井保证无漏水点、玻璃钢井底垫层100mm厚、周围需垫砂200mm厚","材料乙供"]
[120,"环保处理中心","除臭间西侧","土建工程","回填撼砂","管道上下及四周","——",25,"m3","——","井及管道周围撼砂","材料乙供"]
[121,"环保处理中心","除臭间西侧","土建工程","安装井盖","检查井盖、座安装 铸铁井盖、座","——",2,"套","——","700轻型井盖（121KG）","材料乙供"]
[122,"环保处理中心","除臭间西侧","土建工程","安装井圈","检查井盖、座安装 混凝土井盖、座","——",2,"个","——","安装混凝土井圈直径1200*700","材料乙供"]
[123,"环保处理中心","除臭间西侧","土建工程","开墙孔","110mm墙洞","——",3,"个","——","受限空间","材料乙供"]
[124,"环保处理中心","除臭间西侧","土建工程","安装卡箍","110m不锈钢卡箍","——",1,"个","——","受限空间","材料乙供"]
[125,"环保处理中心","除臭间西侧","土建工程","机械碾压 原土，铺石子","机械碾压 原土，铺石子10cm","——",150,"m2","——","人工回填碾压石灰土200mm厚、需使用斗容量1m3履带钩机挖土及回填，进出场需拖板车拖运一台次，人工配合2工日","材料乙供"]
[126,"环保处理中心","除臭间西侧","土建工程","残土外运","自卸车15km厂外","——",1,"台班",null,"装载机1m3 1台班配合装车","材料乙供"]
[127,"环保处理中心","除臭间西侧","土建工程","安装管道","安装DN1000玻璃钢管（承重力8KN）","——",5,"m",null,"井及管道周围撼砂、水撼砂振动棒配合18m2","材料乙供"]
[128,"环保处理中心","除臭间西侧","土建工程","安装管道","安装DN400玻璃钢管（承重力8KN）","——",12,"m",null,"井及管道周围撼砂、水撼砂振动棒配合18m2","材料乙供"]
[129,"环保处理中心","除臭间西侧","土建工程","更换玻璃钢井","拆除原有DN800*2000mm砖砌井、更换安装DN1000*2000","——",1,"座",null,"拆除原有渗漏井、更换安装的玻璃钢井保证无漏水点、玻璃钢井底垫层100mm厚、周围需垫砂200mm厚","材料乙供"]
[130,"环保处理中心","除臭间西侧","土建工程","安装井盖","拆除更换检查井盖、座安装 铸铁井盖、座","——",3,"套",null,"更换700轻型井盖（121KG）","材料乙供"]
[131,"环保处理中心","除臭间西侧","土建工程","安装混凝土井圈","安装混凝土井圈直径1200*700","——",3,"套",null,"安装混凝土井圈直径1200mm*700mm","材料乙供"]
[132,"环保处理中心","除臭间西侧","土建工程","保温拆除","拆除外墙保温50厚","——",49,"m2",null,"拆除物清理、垃圾外运1车(规格10m3）","材料乙供"]
[133,"环保处理中心","除臭间西侧","土建工程","拆除墙皮","拆除外墙水泥砂浆20厚","——",49,"m2",null,"拆除墙皮找漏、垃圾外运1车(规格10m3）","材料乙供"]
[134,"环保处理中心","除臭间西侧","土建工程","灌浆堵漏","拆除墙皮找漏点打针聚氨酯","——",50,"个",null,"灌浆堵漏","材料乙供"]
[135,"环保处理中心","除臭间西侧","土建工程","抹灰","打针试水不漏抹灰20厚","——",49,"m2","——","水泥砂浆找平","材料乙供"]
[136,"环保处理中心","除臭间西侧","土建工程","保温恢复","墙面 挤塑板厚度 50mm","——",49,"m2",null,"墙面 聚苯乙烯板 厚度 50mm30kg/m3","材料乙供"]
[137,"环保处理中心","除臭间西侧","土建工程","抹胶泥","墙面 抗裂保护层 玻纤网格布抗裂砂浆 厚度 4mm","——",49,"m2","——","搭设脚手架5m高","材料乙供"]
[138,"环保处理中心","除臭间西侧","土建工程","刷涂料","刷抗碱底涂料刮外墙腻子2遍刷涂料二遍","——",49,"m2","——","分层刷涂","材料乙供"]
[139,"环保处理中心","除臭间西侧","土建工程","钢质防火门安装","防火门拆除安装","——",3,"m2","——","拆除物清理","材料乙供"]
[140,"环保处理中心","除臭间西侧","土建工程","装载机装车 土方","装填拉运残土60m3","——",3,"台班","——","需使用装载机1m3约台班配合装车、使用20t自卸车外运至场外15km","材料乙供"]
[141,"环保处理中心","除臭间西侧","土建工程","机械碾压 原土，铺石子","回填土方50m3","——",50,"m2","——","回填土夯实后铺设195m2石子","材料乙供"]
[142,"环保处理中心","除臭间西侧","土建工程","铺石灰土","人工回填碾压石灰土200mm厚","——",195,"m2","——","需机械配合施工","材料乙供"]
[143,"环保处理中心","环保办公楼三楼卫生间","土建工程","塑钢窗维修","塑钢窗扇1160mm*760mm维修，更换折页、滑道、窗把手，重新固定修复。","——",1,"扇","——","修复后开关自如，无卡顿，密封严实","材料乙供"]
[144,"环保处理中心","环保办公楼三楼化验室","土建工程","塑钢窗维修","塑钢窗扇1160mm*760mm维修，更换折页、滑道、窗把手，更换密封胶条，重新固定修复，开关自如","——",4,"扇","——","修复后开关自如，无卡顿，密封严实","材料乙供"]
[145,"环保处理中心","环保办公楼三楼会议室","土建工程","更换钢化玻璃","三楼外窗玻璃710mm*1330mm，四周打胶，登高安装","——",2,"扇","——","高层外窗，高度约8m，考虑安装位置","材料乙供"]
[146,"环保处理中心","环保办公楼一楼","土建工程","玻璃雨搭","一楼玻璃雨搭破损开裂钢化玻璃拆除后更换新玻璃雨搭","——",6,"m2","——","户外，一楼约2.5m，考虑安装位置","材料乙供"]
[147,"环保处理中心","污泥干化","土建工程","搭设脚手架","搭设4m*4m*8m架子维修干化机","——",4,"个","——","搭设架子需配有合格证","材料乙供"]
[148,"环保处理中心","酸水中和岗位","土建工程","预处理间配电室门维修","0.8X2米门框加固，门把手维修，门锁更换","——",1.6,"m2","——","施工后门开闭自如，无卡顿","材料乙供"]
[149,"环保处理中心","高浓度废水","土建工程","搭设脚手架","搭设木质脚手架6m*3m*8m","——",6,"个","——","搭设架子需配有合格证","材料乙供"]
[150,"环保处理中心","含磷废水","土建工程","搭设脚手架","搭设钢制脚手架2m*2m*4m","——",4,"个","——","搭设架子需配有合格证","材料乙供"]
[151,"研究院","分析化验中心","土建工程","更换水龙头","实验室洗水池水龙头（DN20）","不锈钢",2,"套","国标","拆除旧龙头，安装新龙头。","材料乙供"]
[152,"研究院","合成中心","土建工程","更换木门贴纸","900mm×2000mm","密度板等",2,"套","国标","木纹纸脱落损坏，贴木纹纸。","材料乙供"]
[153,"研究院","分析化验中心","土建工程","更换木门折页","通道木门折页老化损坏","密度板等",2,"套","国标","维修后通道门可以正常开关。","材料乙供"]
[154,"研究院","合成中心","土建工程","更换窗户把手","——","断桥铝",3,"套","国标","拆除旧把手，安装新把手。","材料乙供"]
[155,"研究院","合成中心","土建工程","更换玻璃门地轴","对开玻璃门地轴老化损坏","铝框、玻璃",1,"套","国标","拆除旧转轴，安装新转轴。","材料乙供"]
[156,"研究院","合成中心","土建工程","更换实验室地砖","600mm×600mm，厚度5mm","陶瓷",19,"平方米","国标","维修后实验室地砖平整可以正常使用。","材料乙供"]
[157,"物流储运中心","物料工段","土建工程","脚手架（活动架）","2m*1.2m*2m","——",6,"座","无","——","摄像头维修"]
[158,"物流储运中心","物料工段","土建工程","脚手架（架管）","3m*3m*6m","——",2,"座","无","——","液位计更换，储罐维修"]
[159,"物流储运中心","物料工段","土建工程","下水疏通","——","——",2,"处","——","——","——"]
[160,"物流储运中心","物料工段","土建工程","玻璃钢维修","糊玻璃钢四布五油","——",5,"㎡","无","四布五油","材料乙供"]
[161,"物流储运中心","物料工段","土建工程","挡鼠板维修","挡鼠板增加槽铝0.6m*2根","——",1,"项","无","将原有挡鼠板切割分成两片，槽铝制作斜角，与原有槽铝贴合无缝隙。","材料乙供"]
[162,"物流储运中心","物料工段","土建工程","挡鼠板维修","挡鼠板增加50mm铝合金角钢0.6m*2根","——",1,"项","无","——","材料乙供"]
[163,"物流储运中心","成品岗位","土建工程","清理地面基层","地面清除松动基层","——",10,"㎡","无","将破损地面切割方形后进行基层清除处理，垃圾清运","材料乙供"]
[164,"物流储运中心","成品岗位","土建工程","自流平地面维修","制作环氧自流平","环氧",50,"㎡","无","维修位置归方处理，打磨后制作地面，垃圾清运","材料乙供"]
[165,"物流储运中心","物料工段","土建工程","积液坑盖板制作","制作玻璃钢盖板","玻璃钢",4,"片","无","800m*800mm*30mm","材料乙供"]
[166,"物流储运中心","物料工段","土建工程","静电地板","机房待安装区域尺寸（2.4m×8m）， PVC 贴面款静电地板600mm×600mm，防火等级≥B1 级，承载能力≥300kg/㎡；","——",1,"项","无","地板表面平整，无划痕、凹陷、变形，拼接缝均匀，边缘切割整齐，密封胶条贴合紧密，无脱落。地板下管线无受压、破损。","材料乙供"]
[167,"物流储运中心","物料工段","土建工程","静电地板","板支架高度 300mm，材质为镀锌钢，地板横梁长度600mm ","——",1,"项","无","配备缓步台阶","材料乙供"]
[168,"物流储运中心","运输工段","土建工程","刷桶积液坑改造","原积液坑回填1200mm*1200mm*1000mm","混凝土",1,"项","——","原有积液坑清掏","材料乙供"]
[169,"物流储运中心","运输工段","土建工程","刷桶积液坑改造","玻璃钢防腐","玻璃钢",3,"㎡","——","玻璃钢防腐，3mm厚","材料乙供"]
[170,"生活服务中心","细河总更","土建工程","排风机","φ600mm*厚300mm","——",2,"台","——","风机拆除安装，高2米。","风机甲供"]
[171,"生活服务中心","细河总更","土建工程","三防板龙骨","厚1.5mm","热镀锌钢板",30,"m","——","拆除安装","材料乙供"]
[172,"生活服务中心","细河食堂","土建工程","排水沟壁砖","600mm*600mm*20mm","理石",30,"m2","——","原损坏壁砖拆除、清理，新铺理石砖、做好防护、 残土外运。","材料乙供"]
[173,"能源保障中心","细河供电工段","土建工程","固定路灯基础","固定路灯基础1个尺寸50*50*100cm","水泥",1,"个","无","固定路灯基础1个尺寸50*50*100cm，恢复路灯杆稳固不摇晃。","材料乙供"]
[174,"能源保障中心","细河供汽工段","土建工程","破碎机间防火门更换","\n对开门，单门尺寸高2.27（m）*宽0.68（m），钢制乙级防火门，耐火极限≥1.5小时。","无",2,"个","无","1更换单门尺寸2.27（m）*0.68（m）两个，左右对开，防火防水防腐蚀阻燃，门开关顺畅，在闭门状态下，门扇与门框贴合，门锁正常。\n2材料乙供。\n3现场清理，清走垃圾。                              4、钢制乙级防火门，耐火极限≥1.5小时。出具型式检验报告。","材料乙供"]
[175,"能源保障中心","细河供汽工段","土建工程","接煤间门更换","\n门尺寸高1.90（m）*0.85（m），钢制乙级防火门，耐火极限≥1小时。","无",1,"个","无","1更换门尺寸1.90*0.85（m），门开关顺畅，在闭门状态下，门扇与门框贴合，门锁正常。\n2材料乙供。\n3现场清理，清走垃圾。                             4、钢制乙级防火门，耐火极限≥1小时。出具型式检验报告。","材料乙供"]
[176,"能源保障中心","细河供汽工段","土建工程","25米层防火门更换","对开门，单门尺寸高2.15（m）*宽0.72（m），钢质乙级防火门。","无",2,"个","无","1更换单门尺寸2.15*0.72（m）两个，左右对开，防火防水防腐蚀阻燃，门开关顺畅，在闭门状态下，门扇与门框贴合，门锁正常。\n2材料乙供。\n3现场清理，清走垃圾。                               4、钢质乙级防火门。出具型式检验报告。","材料乙供"]
[177,"能源保障中心","细河供汽工段","土建工程","锅炉主厂房外墙\n雨水管维修","作业高度最高35米。\n雨排管直径170mm。","雨排管聚氯乙烯(PVC)",30,"m","无","1.对雨排管路损坏部分进行更换和固定。\n2.现场清理，清走垃圾。                           3.更换雨排管30米。","材料乙供"]
[178,"能源保障中心","细河供汽工段","土建工程","2号脱硫塔维修\n搭脚手架","长3米*宽2米*高10米","——",1,"座","无","1、脚手架\n2、符合安全要求","材料乙供"]
[179,"能源保障中心","细河供汽工段","土建工程","污水井管路疏通","玻璃钢管路DN200","-",40,"米","无","1.污水管距井口1.5米。\n2.污水井恢复正常排水、水流顺畅。\n3.淤泥和淤堵垃圾清运出厂。","-"]
[180,"能源保障中心","细河供汽工段","土建工程","清掏污水井","清掏污水井淤泥","-",10,"m³","无","1、清掏污水井淤泥。2、清掏垃圾清运出厂。","-"]
[181,"能源保障中心","细河供水工段","土建工程","贴瓷砖","E200一级水厂房墙面贴瓷砖","瓷砖",5.4,"㎡","无","冷冻厂房内墙面贴瓷砖，瓷砖尺寸60*30（cm），高度0-2米，2年内无开裂，要求：原瓷砖离缝，把原瓷砖无破坏的拆下来","材料乙供"]
[182,"能源保障中心","细河供水工段","土建工程","操作室门维修","\n门尺寸2.10（m）*1.50（m）","无",2,"个","无","维修两道门尺寸2.10*1.50（m），关不严，门锁坏，要求：不能暴力，保留门的完整性，门开关顺畅，门锁正常","材料乙供"]
[183,"能源保障中心","细河供水工段","土建工程","雨水管维修","挖沟5m长*1m宽*1m深","无",5,"m³","无","冷冻厂房北侧雨水管进雨水井段挖开，断开处接好，回填，恢复原状。挖填回填，恢复地面。","材料乙供"]
[184,"能源保障中心","细河供水工段","土建工程","雨水管维修","DN150地埋进雨水井雨水管更换","无",5,"m","无","冷冻厂房北侧雨水管进雨水井段挖开，断开处接好，","材料乙供"]
[185,"能源保障中心","细河供水工段","土建工程","窗户","1.1（m)*0.6（m)","窗户",1,"扇","无","窗户脱落，重新安装折页，更换一扇新窗户，要求：开关正常","材料乙供"]